## VSPA
Variable Speed Pump Analysis (VSPAnalysis) - for applications with positive or negative suction pressure
[6 empty] | Joe Evans, Ph.D 3/17/2015 |  |  |  | http://www.PumpEd101.com |  |  |  | http://www.PumpTechnw.com
Follow the steps below to view the operating characteristics of a centrifugal pump with +/- suction pressure under VFD control.
[6 empty] | 1) Enter the pump description in the yellow box to the right. | [7 empty] | Cornell 5RB 1780 RPM 13.5" Trim
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 | [7 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
[6 empty] | 2) (For fewer than eight points, enter the last value multiple | [7 empty] | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000 | 2250
times. Do the same for steps 3 & 4).
[6 empty] | 3) Enter the corresponding heads (in ft) in H1 - H8 | [7 empty] | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
[6 empty] | that correspond to the flows in Q1 - Q8. | [7 empty] | 200 | 195 | 187 | 178 | 165 | 148 | 125 | 100
60 | 3600 | 100% | 100% | 100% |  | Calculated Total Head (Pump Head + Suction Head) | [7 empty] | 212 | 207 | 199 | 190 | 177 | 160 | 137 | 112
[6 empty] | 4) Enter the pump's hydraulic efficiencies (.xx) in Ef 1 - Ef 8 | [7 empty] | Ef 1 | Ef 2 | Ef 3 | Ef 4 | Ef 5 | Ef 6 | Ef 7 | Ef 8
[6 empty] | that correspond to the flows in Q1 - Q8. | [7 empty] | 0.6 | 0.72 | 0.8 | 0.84 | 0.86 | 0.86 | 0.83 | 0.74
[6 empty] | 5) Enter the pump's suction pressure in feet in cell Ps | [7 empty] | Ef 1: Ps; Ef 2: 12
If it is negative, enter -xx.
[6 empty] | 6) To plot a system or constant pressure curve, enter the | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | system heads (in ft) in SH1 - SH8 that correspond to the | [7 empty] | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
flows in Q1 - Q8.
http://www.PumpEd101.com
HP Calculations
[22 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
[5 empty] | 60 | 60hz calculated from data input | [15 empty] | 44.6128 | 54.4508 | 62.8157 | 71.3985 | 77.9598 | 82.2175 | 83.3638 | 85.9951
59 | 3540 | 98.33% | 96.69% | 95.08% | 59 | 491.6667 | 737.5 | 983.3333 | 1229.1667 | 1475 | 1720.8333 | 1966.6667 | 2212.5 | 204.9922 | 200.1575 | 192.4219 | 183.7194 | 171.1492 | 154.7111 | 132.4714 | 108.2978 | [8 empty] | kW / 1000 gal Calculations | [7 empty] | $$ / 1000 gal Calculations
58 | 3480 | 96.67% | 93.44% | 90.33% | 58 | 483.3333 | 725 | 966.6667 | 1208.3333 | 1450 | 1691.6667 | 1933.3333 | 2175 | 198.1022 | 193.43 | 185.9544 | 177.5444 | 165.3967 | 149.5111 | 128.0189 | 104.6578 | 40.2986 | 49.1852 | 56.7411 | 64.494 | 70.4208 | 74.2668 | 75.3022 | 77.679
57 | 3420 | 95% | 90.25% | 85.74% | 57 | 475 | 712.5 | 950 | 1187.5 | 1425 | 1662.5 | 1900 | 2137.5 | 191.33 | 186.8175 | 179.5975 | 171.475 | 159.7425 | 144.4 | 123.6425 | 101.08 | [8 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
56 | 3360 | 93.33% | 87.11% | 81.3% | 56 | 466.6667 | 700 | 933.3333 | 1166.6667 | 1400 | 1633.3333 | 1866.6667 | 2100 | 184.6756 | 180.32 | 173.3511 | 165.5111 | 154.1867 | 139.3778 | 119.3422 | 97.5644 | 36.2719 | 44.2705 | 51.0715 | 58.0496 | 63.3842 | 66.8459 | 67.7778 | 69.9172
55 | 3300 | 91.67% | 84.03% | 77.03% | 55 | 458.3333 | 687.5 | 916.6667 | 1145.8333 | 1375 | 1604.1667 | 1833.3333 | 2062.5 | 178.1389 | 173.9375 | 167.2153 | 159.6528 | 148.7292 | 134.4444 | 115.1181 | 94.1111 | 34.3632 | 41.9409 | 48.3841 | 54.995 | 60.0489 | 63.3284 | 64.2113 | 66.2381 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
54 | 3240 | 90% | 81% | 72.9% | 54 | 450 | 675 | 900 | 1125 | 1350 | 1575 | 1800 | 2025 | 171.72 | 167.67 | 161.19 | 153.9 | 143.37 | 129.6 | 110.97 | 90.72 | 32.5227 | 39.6946 | 45.7926 | 52.0495 | 56.8327 | 59.9366 | 60.7722 | 62.6904
53 | 3180 | 88.33% | 78.03% | 68.92% | 53 | 441.6667 | 662.5 | 883.3333 | 1104.1667 | 1325 | 1545.8333 | 1766.6667 | 1987.5 | 165.4189 | 161.5175 | 155.2753 | 148.2528 | 138.1092 | 124.8444 | 106.8981 | 87.3911
52 | 3120 | 86.67% | 75.11% | 65.1% | 52 | 433.3333 | 650 | 866.6667 | 1083.3333 | 1300 | 1516.6667 | 1733.3333 | 1950 | 159.2356 | 155.48 | 149.4711 | 142.7111 | 132.9467 | 120.1778 | 102.9022 | 84.1244 | 29.0413 | 35.4454 | 40.8907 | 46.4778 | 50.749 | 53.5206 | 54.2667 | 55.9796
51 | 3060 | 85% | 72.25% | 61.41% | 51 | 425 | 637.5 | 850 | 1062.5 | 1275 | 1487.5 | 1700 | 1912.5 | 153.17 | 149.5575 | 143.7775 | 137.275 | 127.8825 | 115.6 | 98.9825 | 80.92
50 | 3000 | 83.33% | 69.44% | 57.87% | 50 | 416.6667 | 625 | 833.3333 | 1041.6667 | 1250 | 1458.3333 | 1666.6667 | 1875 | 147.2222 | 143.75 | 138.1944 | 131.9444 | 122.9167 | 111.1111 | 95.1389 | 77.7778 | 25.8176 | 31.5109 | 36.3517 | 41.3186 | 45.1156 | 47.5796 | 48.2429 | 49.7657 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
49 | 2940 | 81.67% | 66.69% | 54.47% | 49 | 408.3333 | 612.5 | 816.6667 | 1020.8333 | 1225 | 1429.1667 | 1633.3333 | 1837.5 | 141.3922 | 138.0575 | 132.7219 | 126.7194 | 118.0492 | 106.7111 | 91.3714 | 74.6978
48 | 2880 | 80% | 64% | 51.2% | 48 | 400 | 600 | 800 | 1000 | 1200 | 1400 | 1600 | 1800 | 135.68 | 132.48 | 127.36 | 121.6 | 113.28 | 102.4 | 87.68 | 71.68 | 22.8418 | 27.8788 | 32.1616 | 36.556 | 39.9154 | 42.0954 | 42.6822 | 44.0295
47 | 2820 | 78.33% | 61.36% | 48.07% | 47 | 391.6667 | 587.5 | 783.3333 | 979.1667 | 1175 | 1370.8333 | 1566.6667 | 1762.5 | 130.0856 | 127.0175 | 122.1086 | 116.5861 | 108.6092 | 98.1778 | 84.0647 | 68.7244
46 | 2760 | 76.67% | 58.78% | 45.06% | 46 | 383.3333 | 575 | 766.6667 | 958.3333 | 1150 | 1341.6667 | 1533.3333 | 1725 | 124.6089 | 121.67 | 116.9678 | 111.6778 | 104.0367 | 94.0444 | 80.5256 | 65.8311 | 20.1038 | 24.5371 | 28.3066 | 32.1743 | 35.131 | 37.0497 | 37.5662 | 38.7519
45 | 2700 | 75% | 56.25% | 42.19% | 45 | 375 | 562.5 | 750 | 937.5 | 1125 | 1312.5 | 1500 | 1687.5 | 119.25 | 116.4375 | 111.9375 | 106.875 | 99.5625 | 90 | 77.0625 | 63 | 18.821 | 22.9714 | 26.5004 | 30.1212 | 32.8893 | 34.6855 | 35.1691 | 36.2792 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
44 | 2640 | 73.33% | 53.78% | 39.44% | 44 | 366.6667 | 550 | 733.3333 | 916.6667 | 1100 | 1283.3333 | 1466.6667 | 1650 | 114.0089 | 111.32 | 107.0178 | 102.1778 | 95.1867 | 86.0444 | 73.6756 | 60.2311 | 17.594 | 21.4738 | 24.7726 | 28.1575 | 30.745 | 32.4242 | 32.8762 | 33.9139
43 | 2580 | 71.67% | 51.36% | 36.81% | 43 | 358.3333 | 537.5 | 716.6667 | 895.8333 | 1075 | 1254.1667 | 1433.3333 | 1612.5 | 108.8856 | 106.3175 | 102.2086 | 97.5861 | 90.9092 | 82.1778 | 70.3647 | 57.5244
42 | 2520 | 70% | 49% | 34.3% | 42 | 350 | 525 | 700 | 875 | 1050 | 1225 | 1400 | 1575 | 103.88 | 101.43 | 97.51 | 93.1 | 86.73 | 78.4 | 67.13 | 54.88 | 15.3022 | 18.6766 | 21.5458 | 24.4897 | 26.7402 | 28.2006 | 28.5938 | 29.4963
41 | 2460 | 68.33% | 46.69% | 31.91% | 41 | 341.6667 | 512.5 | 683.3333 | 854.1667 | 1025 | 1195.8333 | 1366.6667 | 1537.5 | 98.9922 | 96.6575 | 92.9219 | 88.7194 | 82.6492 | 74.7111 | 63.9714 | 52.2978
40 | 2400 | 66.67% | 44.44% | 29.63% | 40 | 333.3333 | 500 | 666.6667 | 833.3333 | 1000 | 1166.6667 | 1333.3333 | 1500 | 94.2222 | 92 | 88.4444 | 84.4444 | 78.6667 | 71.1111 | 60.8889 | 49.7778 | 13.2186 | 16.1336 | 18.612 | 21.1551 | 23.0992 | 24.3607 | 24.7004 | 25.48 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
39 | 2340 | 65% | 42.25% | 27.46% | 39 | 325 | 487.5 | 650 | 812.5 | 975 | 1137.5 | 1300 | 1462.5 | 89.57 | 87.4575 | 84.0775 | 80.275 | 74.7825 | 67.6 | 57.8825 | 47.32
38 | 2280 | 63.33% | 40.11% | 25.4% | 38 | 316.6667 | 475 | 633.3333 | 791.6667 | 950 | 1108.3333 | 1266.6667 | 1425 | 85.0356 | 83.03 | 79.8211 | 76.2111 | 70.9967 | 64.1778 | 54.9522 | 44.9244
37 | 2220 | 61.67% | 38.03% | 23.45% | 37 | 308.3333 | 462.5 | 616.6667 | 770.8333 | 925 | 1079.1667 | 1233.3333 | 1387.5 | 80.6189 | 78.7175 | 75.6753 | 72.2528 | 67.3092 | 60.8444 | 52.0981 | 42.5911
36 | 2160 | 60% | 36% | 21.6% | 36 | 300 | 450 | 600 | 750 | 900 | 1050 | 1200 | 1350 | 76.32 | 74.52 | 71.64 | 68.4 | 63.72 | 57.6 | 49.32 | 40.32
35 | 2100 | 58.33% | 34.03% | 19.85% | 35 | 291.6667 | 437.5 | 583.3333 | 729.1667 | 875 | 1020.8333 | 1166.6667 | 1312.5 | 72.1389 | 70.4375 | 67.7153 | 64.6528 | 60.2292 | 54.4444 | 46.6181 | 38.1111 | 8.8554 | 10.8082 | 12.4686 | 14.1723 | 15.4747 | 16.3198 | 16.5473 | 17.0696 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
34 | 2040 | 56.67% | 32.11% | 18.2% | 34 | 283.3333 | 425 | 566.6667 | 708.3333 | 850 | 991.6667 | 1133.3333 | 1275 | 68.0756 | 66.47 | 63.9011 | 61.0111 | 56.8367 | 51.3778 | 43.9922 | 35.9644
33 | 1980 | 55% | 30.25% | 16.64% | 33 | 275 | 412.5 | 550 | 687.5 | 825 | 962.5 | 1100 | 1237.5 | 64.13 | 62.6175 | 60.1975 | 57.475 | 53.5425 | 48.4 | 41.4425 | 33.88
32 | 1920 | 53.33% | 28.44% | 15.17% | 32 | 266.6667 | 400 | 533.3333 | 666.6667 | 800 | 933.3333 | 1066.6667 | 1200 | 60.3022 | 58.88 | 56.6044 | 54.0444 | 50.3467 | 45.5111 | 38.9689 | 31.8578
31 | 1860 | 51.67% | 26.69% | 13.79% | 31 | 258.3333 | 387.5 | 516.6667 | 645.8333 | 775 | 904.1667 | 1033.3333 | 1162.5 | 56.5922 | 55.2575 | 53.1219 | 50.7194 | 47.2492 | 42.7111 | 36.5714 | 29.8978
30 | 1800 | 50% | 25% | 12.5% | 30 | 250 | 375 | 500 | 625 | 750 | 875 | 1000 | 1125 | 53 | 51.75 | 49.75 | 47.5 | 44.25 | 40 | 34.25 | 28 | 5.5766 | 6.8063 | 7.852 | 8.9248 | 9.745 | 10.2772 | 10.4205 | 10.7494 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[7 empty] | 100 | 77 | 58
[19 empty] | System Curve Flow |  |  | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000 | 2250
[19 empty] | System Curve Head |  |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
[6 empty] | % Eff | 60% | 72% | 80% | 84% | 86% | 86% | 83% | 74% |  |  |  |  | System Curve BHP |  |  | 42.0875 | 52.6094 | 63.1313 | 75.1563 | 88.0902 | 102.7719 | 121.6989 | 153.5627