## VSPA
Variable Speed Pump Analysis (VSPAnalysis) - with Autoplot
[6 empty] | Joe Evans, Ph.D 10/1/2010 |  |  |  | http://www.PumpEd101.com |  |  |  | http://www.PumpTechnw.com
Follow the steps below to view the operating characteristics and potential power savings of a centrifugal pump under VFD control.
Scroll down for more detailed instructions and an explaination of the included example.
[6 empty] | 1) Enter the pump description in the yellow box to the right | [7 empty] | Cornell 5RB 1780 RPM 13.5" Trim
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 | [7 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
[6 empty] | 2) See instructions for fewer than eight points | [7 empty] | 260 | 520 | 650 | 780 | 910 | 1040 | 1170 | 1300
[6 empty] | Enter the corresponding heads (in ft) in H1 - H8 | [7 empty] | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
60 | 3600 | 100% | 100% | 100% | [9 empty] | 86 | 83 | 81 | 78 | 75 | 71 | 66 | 61
[6 empty] | 3) Enter the pump's hydraulic efficiencies (.xx) in Ef 1 - Ef 8 | [7 empty] | Ef 1 | Ef 2 | Ef 3 | Ef 4 | Ef 5 | Ef 6 | Ef 7 | Ef 8
[6 empty] | that correspond to the flows in Q1 - Q8. | [7 empty] | 0.45 | 0.6 | 0.68 | 0.74 | 0.78 | 0.81 | 0.74 | 0.65
[6 empty] | 4) Enter the design point flow, head & Ef (.xx) in Qd, Hd & Efd | [7 empty] | Qd | 1130 | Hd | 71 | Efd | 0.81
[6 empty] | 5) Enter BEP Q, H, Ef (.xx) & NPSHr in Qb, Hb, Efb & Nrb | [7 empty] | Qb | 1130 | Hb | 71 | Efb | 0.81 | Nrb | 8.3
[6 empty] | 6) Enter motor efficiency (.xx) in Efm, speed (RPM) in RPM | [7 empty] | Efm | 0.9 | RPM | 1850 |  |  | $/kWH | 0.1
and electrical power cost per kWH (.xxx) in $/kWH
[6 empty] | 7) To plot a system or constant pressure curve, enter the | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | system heads (in ft) in SH1 - SH8 that correspond to the | [7 empty] | 125 | 125 | 125 | 127 | 130 | 137 | 147 | 162
flows in Q1 - Q8. (See Instructions below)
| AFFINITY LAW CALCULATOR |  |  |  |  | VSPA Instructions
The Variable Speed Pump Analysis spreadsheet produces five charts that will allow you to evaluate the performance of a pump and
its H/Q in a particular application. Pump Head and Pump Efficiency will show you how well the curve will meet your desired flow
range. Pump BHP, kW per 1000 gal and Cost per 1000 gal will allow you to evaluate power consumption and savings. The
Useful Calculations tab automatically computes Specific Speed, Suction Specific Speed, and several conditions at BEP and
the design point. Once you have decided on the best pump, download VFPPA from my web site and use it to determine
whether individual or synchronous speed control is best for multiple pump operation.
Step 1
Enter the pump description as you would like it to appear on the charts.
Step 2
| Enter a motor speed for 60 Hz |  |  |  |  | Auto Plot requires that you enter eight, 60 Hz operating points in the row with the yellow background. Flows are entered
| operation in the cell with the |  |  |  |  | beneath Q1 - Q8 and the corresponding heads are entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor |  |  |  |  | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point from
| speeds at the lower frequencies |  |  |  |  | 59 - 30 Hz, however, Auto Plot displays the curves in 5hz increments (i.e. 55, 50, 45, etc). The labels displayed at each
| will be displayed. Note that the |  |  |  |  | xy intercept on the head / capacity curves is differenc for each chart that is plotted. *If you wish to enter fewer than eight
points, enter the last point multiple times. For example if you have only six points, enter the data in Q6/H6 again in both
Q7/H7 and Q8/H8. The same will hold true for Steps 3 & 7.
Step 3
Enter the pump's hydraulic efficiency in Ef1 through Ef8. Enter the value as a decimal. When entering fewer
than 8 points, follow the directions in Step 2.
Step 4
Enter the design point flow, head and hydraulic efficiency in the proper cells. Enter efficiency as a decimal.
Step 5
Enter the Best Efficiency Point flow, head and hydraulic efficiency in the proper cells. Enter efficiency as a decimal.
Step 6
Enter the electric motor efficiency, speed in RPM and the cost per kilowatt hour charged by the local utility.
Enter efficiency and kWH cost as a decimal. Three decimal places are provided for cost as many utilitiy rates
include a fraction of a cent.
Step 7
Generate a system curve for the application and enter the values in SH1 through SH8. These may be a flat curve for
pressure booster applications or a combination of static head and friction. Calculate the system head for each flow
point Q1 through Q8. If you are entering fewer than 8 points follow the directions in Step 2
Step 8
If the selected pump will be running in parallel with an identical pump, copy the flow, head, efficiency and system
curve data and paste in into VFPPA. Use VFPPA to determine whether to use synchronous or individual speed
control during operation of the pumps.
The Example
The VSPA example shows a pump operating at a static head of 125' and additional friction head that kicks in at flows
over 1000 gpm. The max flow design point is 1850 gpm @ 140' which is to the right of BEP but within the acceptable
operating range. The application requires variable speed flows from 1000 to 1850 gpm.
The "Pump Head" chart shows that the pump will produce 1000 to 1850gpm over a speed range of 50 to 60hz. This
10hz range is more than adequate to keep the VFD from "hunting". If it were only 5hz you would probably want to
evaluate another pump.
The "Pump Efficiency" chart shows the slope of the efficiency isomers at each flow point. At a low flow of 1000gpm
hydraulic efficiency is 84% and at max flow it is 85%. At intermediate flows it is 86%. This wide efficiency range
will makes this pump a good choice. Even at a flow of 800gpm it still maintains 80% efficiency.
The "Pump BHP" chart shows the hp required across the pumping range and also shows the hp savings obtained
through variable speed vs a control valve. Variable speed hp ranges from 39 to 76 while control valve hp ranges
from 59 to 76. Even at 1500gpm there is a 15hp reduction with variable speed vs a control valve.
The "kW per 1000 Gal" chart takes BHP a step further and shows the energy required to pump 1000 gallons. It
ranges from 0.51 kW at 1000gpm to about 0.57 kW at full flow.
The "Cost per 1000 Gal" chart shows the actual cost to pump 1000 gallons at various points based upon the utility
kWH charge that was entered. It ranges from $0.051 at 1000gpm to $0.057 at full flow.
The "Useful Calculations" tab contains several calculations including Specific Speed, Suction Specific Speed and
some BEP and Design Point information. You can add more if you like. You will note that the Nss calculation is
is fairly high and could indicate flow reversal in the eye at flows below BEP. But Nss is directly proportional to
pump speed and if you calculate it at the lower speeds, you will see that it drops proportionally.
http://www.PumpEd101.com
59 | 3540 | 98.33% | 96.69% | 95.08% | 59 | 255.6667 | 511.3333 | 639.1667 | 767 | 894.8333 | 1022.6667 | 1150.5 | 1278.3333 | 83.1572 | 80.2564 | 78.3225 | 75.4217 | 72.5208 | 68.6531 | 63.8183 | 58.9836 |  | HP Calculations | [6 empty] | kW / 1000 gal Calculations | [7 empty] | $$ / 1000 gal Calculations
58 | 3480 | 96.67% | 93.44% | 90.33% | 58 | 251.3333 | 502.6667 | 628.3333 | 754 | 879.6667 | 1005.3333 | 1131 | 1256.6667 | 80.3622 | 77.5589 | 75.69 | 72.8867 | 70.0833 | 66.3456 | 61.6733 | 57.0011 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
57 | 3420 | 95% | 90.25% | 85.74% | 57 | 247 | 494 | 617.5 | 741 | 864.5 | 988 | 1111.5 | 1235 | 77.615 | 74.9075 | 73.1025 | 70.395 | 67.6875 | 64.0775 | 59.565 | 55.0525 | 12.5477 | 18.165 | 19.5521 | 20.7617 | 22.096 | 23.0203 | 26.3514 | 30.8081 | 0.66671 | 0.48259 | 0.41555 | 0.36772 | 0.33544 | 0.30579 | 0.31114 | 0.32739 | 0.066671 | 0.048259 | 0.041555 | 0.036772 | 0.033544 | 0.030579 | 0.031114 | 0.032739
56 | 3360 | 93.33% | 87.11% | 81.3% | 56 | 242.6667 | 485.3333 | 606.6667 | 728 | 849.3333 | 970.6667 | 1092 | 1213.3333 | 74.9156 | 72.3022 | 70.56 | 67.9467 | 65.3333 | 61.8489 | 57.4933 | 53.1378
55 | 3300 | 91.67% | 84.03% | 77.03% | 55 | 238.3333 | 476.6667 | 595.8333 | 715 | 834.1667 | 953.3333 | 1072.5 | 1191.6667 | 72.2639 | 69.7431 | 68.0625 | 65.5417 | 63.0208 | 59.6597 | 55.4583 | 51.2569 | 9.6649 | 13.9917 | 15.0601 | 15.9918 | 17.0195 | 17.7315 | 20.2973 | 23.7301 | 0.56022 | 0.40551 | 0.34918 | 0.30898 | 0.28186 | 0.25695 | 0.26145 | 0.2751 | 0.056022 | 0.040551 | 0.034918 | 0.030898 | 0.028186 | 0.025695 | 0.026145 | 0.02751
54 | 3240 | 90% | 81% | 72.9% | 54 | 234 | 468 | 585 | 702 | 819 | 936 | 1053 | 1170 | 69.66 | 67.23 | 65.61 | 63.18 | 60.75 | 57.51 | 53.46 | 49.41
53 | 3180 | 88.33% | 78.03% | 68.92% | 53 | 229.6667 | 459.3333 | 574.1667 | 689 | 803.8333 | 918.6667 | 1033.5 | 1148.3333 | 67.1039 | 64.7631 | 63.2025 | 60.8617 | 58.5208 | 55.3997 | 51.4983 | 47.5969
52 | 3120 | 86.67% | 75.11% | 65.1% | 52 | 225.3333 | 450.6667 | 563.3333 | 676 | 788.6667 | 901.3333 | 1014 | 1126.6667 | 64.5956 | 62.3422 | 60.84 | 58.5867 | 56.3333 | 53.3289 | 49.5733 | 45.8178
51 | 3060 | 85% | 72.25% | 61.41% | 51 | 221 | 442 | 552.5 | 663 | 773.5 | 884 | 994.5 | 1105 | 62.135 | 59.9675 | 58.5225 | 56.355 | 54.1875 | 51.2975 | 47.685 | 44.0725
50 | 3000 | 83.33% | 69.44% | 57.87% | 50 | 216.6667 | 433.3333 | 541.6667 | 650 | 758.3333 | 866.6667 | 975 | 1083.3333 | 59.7222 | 57.6389 | 56.25 | 54.1667 | 52.0833 | 49.3056 | 45.8333 | 42.3611 | 7.2614 | 10.5121 | 11.3149 | 12.0149 | 12.787 | 13.3219 | 15.2496 | 17.8288 | 0.46299 | 0.33513 | 0.28858 | 0.25536 | 0.23295 | 0.21235 | 0.21607 | 0.22735 | 0.046299 | 0.033513 | 0.028858 | 0.025536 | 0.023295 | 0.021235 | 0.021607 | 0.022735
49 | 2940 | 81.67% | 66.69% | 54.47% | 49 | 212.3333 | 424.6667 | 530.8333 | 637 | 743.1667 | 849.3333 | 955.5 | 1061.6667 | 57.3572 | 55.3564 | 54.0225 | 52.0217 | 50.0208 | 47.3531 | 44.0183 | 40.6836
48 | 2880 | 80% | 64% | 51.2% | 48 | 208 | 416 | 520 | 624 | 728 | 832 | 936 | 1040 | 55.04 | 53.12 | 51.84 | 49.92 | 48 | 45.44 | 42.24 | 39.04
47 | 2820 | 78.33% | 61.36% | 48.07% | 47 | 203.6667 | 407.3333 | 509.1667 | 611 | 712.8333 | 814.6667 | 916.5 | 1018.3333 | 52.7706 | 50.9297 | 49.7025 | 47.8617 | 46.0208 | 43.5664 | 40.4983 | 37.4303
46 | 2760 | 76.67% | 58.78% | 45.06% | 46 | 199.3333 | 398.6667 | 498.3333 | 598 | 697.6667 | 797.3333 | 897 | 996.6667 | 50.5489 | 48.7856 | 47.61 | 45.8467 | 44.0833 | 41.7322 | 38.7933 | 35.8544
45 | 2700 | 75% | 56.25% | 42.19% | 45 | 195 | 390 | 487.5 | 585 | 682.5 | 780 | 877.5 | 975 | 48.375 | 46.6875 | 45.5625 | 43.875 | 42.1875 | 39.9375 | 37.125 | 34.3125 | 5.2936 | 7.6634 | 8.2486 | 8.7588 | 9.3217 | 9.7117 | 11.117 | 12.9972 | 0.37502 | 0.27146 | 0.23375 | 0.20684 | 0.18869 | 0.17201 | 0.17502 | 0.18416 | 0.037502 | 0.027146 | 0.023375 | 0.020684 | 0.018869 | 0.017201 | 0.017502 | 0.018416
44 | 2640 | 73.33% | 53.78% | 39.44% | 44 | 190.6667 | 381.3333 | 476.6667 | 572 | 667.3333 | 762.6667 | 858 | 953.3333 | 46.2489 | 44.6356 | 43.56 | 41.9467 | 40.3333 | 38.1822 | 35.4933 | 32.8044
43 | 2580 | 71.67% | 51.36% | 36.81% | 43 | 186.3333 | 372.6667 | 465.8333 | 559 | 652.1667 | 745.3333 | 838.5 | 931.6667 | 44.1706 | 42.6297 | 41.6025 | 40.0617 | 38.5208 | 36.4664 | 33.8983 | 31.3303
42 | 2520 | 70% | 49% | 34.3% | 42 | 182 | 364 | 455 | 546 | 637 | 728 | 819 | 910 | 42.14 | 40.67 | 39.69 | 38.22 | 36.75 | 34.79 | 32.34 | 29.89
41 | 2460 | 68.33% | 46.69% | 31.91% | 41 | 177.6667 | 355.3333 | 444.1667 | 533 | 621.8333 | 710.6667 | 799.5 | 888.3333 | 40.1572 | 38.7564 | 37.8225 | 36.4217 | 35.0208 | 33.1531 | 30.8183 | 28.4836
40 | 2400 | 66.67% | 44.44% | 29.63% | 40 | 173.3333 | 346.6667 | 433.3333 | 520 | 606.6667 | 693.3333 | 780 | 866.6667 | 38.2222 | 36.8889 | 36 | 34.6667 | 33.3333 | 31.5556 | 29.3333 | 27.1111 | 3.7178 | 5.3822 | 5.7932 | 6.1516 | 6.547 | 6.8208 | 7.8078 | 9.1283 | 0.29631 | 0.21448 | 0.18469 | 0.16343 | 0.14909 | 0.13591 | 0.13829 | 0.14551 | 0.029631 | 0.021448 | 0.018469 | 0.016343 | 0.014909 | 0.013591 | 0.013829 | 0.014551
39 | 2340 | 65% | 42.25% | 27.46% | 39 | 169 | 338 | 422.5 | 507 | 591.5 | 676 | 760.5 | 845 | 36.335 | 35.0675 | 34.2225 | 32.955 | 31.6875 | 29.9975 | 27.885 | 25.7725
38 | 2280 | 63.33% | 40.11% | 25.4% | 38 | 164.6667 | 329.3333 | 411.6667 | 494 | 576.3333 | 658.6667 | 741 | 823.3333 | 34.4956 | 33.2922 | 32.49 | 31.2867 | 30.0833 | 28.4789 | 26.4733 | 24.4678
37 | 2220 | 61.67% | 38.03% | 23.45% | 37 | 160.3333 | 320.6667 | 400.8333 | 481 | 561.1667 | 641.3333 | 721.5 | 801.6667 | 32.7039 | 31.5631 | 30.8025 | 29.6617 | 28.5208 | 26.9997 | 25.0983 | 23.1969
36 | 2160 | 60% | 36% | 21.6% | 36 | 156 | 312 | 390 | 468 | 546 | 624 | 702 | 780 | 30.96 | 29.88 | 29.16 | 28.08 | 27 | 25.56 | 23.76 | 21.96
35 | 2100 | 58.33% | 34.03% | 19.85% | 35 | 151.6667 | 303.3333 | 379.1667 | 455 | 530.8333 | 606.6667 | 682.5 | 758.3333 | 29.2639 | 28.2431 | 27.5625 | 26.5417 | 25.5208 | 24.1597 | 22.4583 | 20.7569 | 2.4907 | 3.6057 | 3.881 | 4.1211 | 4.3859 | 4.5694 | 5.2306 | 6.1153 | 0.22687 | 0.16421 | 0.1414 | 0.12513 | 0.11414 | 0.10405 | 0.10588 | 0.1114 | 0.022687 | 0.016421 | 0.01414 | 0.012513 | 0.011414 | 0.010405 | 0.010588 | 0.01114
34 | 2040 | 56.67% | 32.11% | 18.2% | 34 | 147.3333 | 294.6667 | 368.3333 | 442 | 515.6667 | 589.3333 | 663 | 736.6667 | 27.6156 | 26.6522 | 26.01 | 25.0467 | 24.0833 | 22.7989 | 21.1933 | 19.5878
33 | 1980 | 55% | 30.25% | 16.64% | 33 | 143 | 286 | 357.5 | 429 | 500.5 | 572 | 643.5 | 715 | 26.015 | 25.1075 | 24.5025 | 23.595 | 22.6875 | 21.4775 | 19.965 | 18.4525
32 | 1920 | 53.33% | 28.44% | 15.17% | 32 | 138.6667 | 277.3333 | 346.6667 | 416 | 485.3333 | 554.6667 | 624 | 693.3333 | 24.4622 | 23.6089 | 23.04 | 22.1867 | 21.3333 | 20.1956 | 18.7733 | 17.3511
31 | 1860 | 51.67% | 26.69% | 13.79% | 31 | 134.3333 | 268.6667 | 335.8333 | 403 | 470.1667 | 537.3333 | 604.5 | 671.6667 | 22.9572 | 22.1564 | 21.6225 | 20.8217 | 20.0208 | 18.9531 | 17.6183 | 16.2836
30 | 1800 | 50% | 25% | 12.5% | 30 | 130 | 260 | 325 | 390 | 455 | 520 | 585 | 650 | 21.5 | 20.75 | 20.25 | 19.5 | 18.75 | 17.75 | 16.5 | 15.25 | 1.5685 | 2.2706 | 2.444 | 2.5952 | 2.762 | 2.8775 | 3.2939 | 3.851 | 0.16668 | 0.12065 | 0.10389 | 0.091929 | 0.08386 | 0.076447 | 0.077786 | 0.081848 | 0.016668 | 0.012065 | 0.010389 | 0.0091929 | 0.008386 | 0.0076447 | 0.0077786 | 0.0081848
[7 empty] | 100 | 77 | 58
[6 empty] | % Eff | 45% | 60% | 68% | 74% | 78% | 81% | 74% | SH1: 65%

## Useful Calculations
Useful Calculations
General |  | BEP
Specific Speed (Ns) | 2542.5365 | Pump Efficiency | 81%
|  | Pump BHP | 25.0125
Suction Specific Speed (Nss)** |  | kW per 1000 Gallons Pumped | 0.30579
60hz | 12717.5186 | Cost per 1000 Gallons Pumped | 0.030579
55hz | 12310.9306
50hz | 11875.2909 | Design Point
45hz | 11416.9567
40hz | 10925.7075 | Pump Efficiency | 81%
35hz | 10387.9079 | Pump BHP | 25.0125
30hz | 9806.5474 | kW per 1000 Gallons Pumped | 0.30579
|  | Cost per 1000 Gallons Pumped | 0.030579
Suction Energy (SE)
Enter eye diameter in inches | 7.2 | If eye diamater is not known it can be
60hz | 169397347.5 | estimated as follows:
55hz | 150371122.7
50hz | 131763002.5 | End Suction - Suction Diameter X 0.9
45hz | 114055397.6 | Split Case - Suction Diameter X 0.75
40hz | 97068792.53
35hz | 80667921.78
30hz | 65311605.78
** NPSHr estimation at reduced speeds is:
(RPM2 / RPM1)^1.5 = (NPSHr2 / NPSHr1)