## Sheet1
Enter the required data in the highlighted cells |  |  | Enter the required data in the highlighted cells
Pump RPM (N) |  | 1770 | Impeller Eye Diameter " (De) |  |  | 9.75
BEP Flow (Q)* |  | 2000 | Pump RPM (N) |  |  | 1770
NPSHr @ BEP |  | 22 | Suction Specific Speed (Nss) |  |  | 7792
|  |  | Specific Gravity (SG) |  |  | 1
S = | 7792.4003 |  | SE = | 134470440
* For double suction pumps enter 1/2 the BEP flow. |  |  | Pump Type |  | High Suction Energy |  | Very High Suction Energy
Values of S greater than 9,000 may require a greater NPSH margin.
Refer to the chart below for acceptable operating ranges. |  |  | 1 or 2- Vane Sewage* |  | 100000000 |  | 150000000
|  |  | End Suction |  | 160000000 |  | 240000000
|  |  | Double Suction |  | 120000000 |  | 180000000
|  |  | Vertical Turbine |  | 200000000 |  | 300000000
* Also any impeller with less than 15⁰ vane overlap
|  |  | Instructions: |  | 1.4873
If the impeller eye diameter is not known it can be approximated as follows:
End Suction Pump - Suction nozzle diameter x 0.90
Horizontal Split Case Pump - Suction nozzle x 0.75
The chart below shows the minimum stable flow for various |  |  | The example used in both calculators is a dry pit non-clog with a 10" suction
specific speeds and suction specific speeds. |  |  | and a two vane, 17.5" impeller. BEP flow is 3400gpm @ 230' and requires
an NPSH of 12 feet.
The chart below shows the NPSH margin required to meed a certain level
of pump reliability. The suction energy ratio is the calculated SE divided
by the high suction energy value for a particular pump design.
S = N √Q / NPSHr0.75
Suction Specific Speed (S or Nss)
Suction Energy (SE)
SE = De x N x S x SG
Suction Calculators Joe Evans www.PumpEd101.com
Window of Operation