## Sheet1
Enter the required data in the highlighted cells. If you do not know the pump
specific speed use the Ns calculator below.
Thrust Factor (KR) @ flow point (from graph) |  | 0.29
Head (H) per Stage @ flow point in feet |  | 138
Specific Gravity (S) |  | 1
Impeller Diameter (D2) in inches |  | 11.88
Impeller Width (b2) @ discharge in inches |  | 3.5
FR (Unbalanced Radial Thrust in lbf) = |  | 720.36
Instructions
Enter the required data in the highlighted cells |  |  | The numbers in ( ) are Pump Specific Speed (Ns). The curves represent the radial thrust factor
from 0 to 120% of BEP flow for that particular specific speed. Select a point on the X axis that
Pump RPM (N) | 2950 |  | corresponds to the point to be evaluated on the pump H/Q curve. The thrust factor is the value
Flow (Q) @ BEP | 1200 |  | on the Y axis where the curve intersects the selected X axis value. For values of Ns that fall
Head (H) @ BEP | 110 |  | between the ones shown you may interpolate the intersection. Impeller width (b2) is the width
Ns = | 3008.6255 |  | in inches at the discharge including the shroud(s). The example shown is for a sewage pump
with a specific speed of 1785, operating at 40% of BEP flow. At 100% of BEP flow, radial thrust is
reduced to 59 lbs. Worst case? This pump is approved by the manufacturer for flows as low as
21% of BEP. At that flow point, radial thrust reaches 660 lbs.
Pump Specific Speed: Ns = N √Q / H0.75
Radial Thrust (PSI): FR = KR x (H x s/2.31) x D2 x b2
Radial Thrust Calculator - Joe Evans www.PumpEd101.com